## Inspection Data
Field | Value
Report ID | VAULT-IR-2026-001
Facility | Engineering Block – Electrical Room E-02
Inspection Date | 08 September 2026
Inspector | R. Kumar, Electrical Maintenance
Overall Status | CONDITIONAL – corrective action required
Panel | Main low-voltage distribution panel
Finding 1 | Feeder-3 terminal showed mild discoloration and should be retorqued after isolation.
Finding 2 | One unused cable entry had an incomplete gland seal.
Finding 3 | Panel interior had moderate dust accumulation.
Finding 4 | Earth continuity label was faded; earthing conductor was physically connected.
Phase-to-phase voltage | 414 V, 412 V, 413 V
Phase-to-neutral voltage | 239 V, 238 V, 240 V
IR testing | Not performed because connected laboratory equipment could not be shut down.
Risk | MEDIUM – localized heating risk at Feeder-3 and possible dust/moisture ingress.
Priority | P2 – corrective maintenance recommended within 7 days.
Recommended action | Isolate Feeder-3, inspect/retorque terminal, replace gland, clean panel, renew label, repeat thermal inspection.